## power-quality-rules
RuleSetNo | RuleNo | Description | Script | DetailText | PerProfile | lock
8 | 7 | Consistency between kVA, V and I - the rule is based on the average voltage, current and average standard deviation voltage and current AND some margin for the accuracy of measuring A | SELECT kva, Dayfield, @RuleSetNo, @RuleNo, kvaavg AS DetailValue FROM PQcrossstats WHERE kva = @Profileid AND kvacnt> 288*0.7 AND (kvaavg*1000 not between (vavg*aavg - vsd*asd)-55 and (vavg*aavg+vsd*asd)+55) | kVA-consistency |  | 0
8 | 8 | Consistency between kVA and kW - the ratio should be between 0.2 and 1 when the average kVA is larger than 0.05 | SELECT kw, Dayfield, @RuleSetNo, @RuleNo, kwavg/kvaavg AS DetailValue FROM PQcrossstats WHERE kw = @Profileid AND kwcnt> 288*0.7 AND (kwavg/kvaavg not between 0.2 and 1) and kvaavg > 0.05 | kW-consistency |  | 0
8 | 1 | Identifies flat spots in channels (1 month where average is less than 0.02 A or max(units read)<0.15A ) | SELECT L.ProfileID, dayfield, @RuleSetNo, @RuleNo, R.mean FROM PQDayStats l INNER JOIN (SELECT DateDiff(mm, 0, DayField) AS Month, AVG(avgunits) mean, MAX(maxunits) maxi FROM PQDayStats p WHERE (ProfileID = @ProfileID) AND ProfileId IN (SELECT ProfileId FROM Profiles WHERE [Unit of measurement] = 2) GROUP BY profileid, DateDiff(mm, 0, DayField) HAVING sum(cntunits)> 0.7* 720 AND AVG(avgUnits) < 0.02 OR MAX(maxUnits) < 0.150) R ON (DateDiff(mm, 0, Dayfield) = R.Month) WHERE L.ProfileID = @ProfileID | I-Flatspot | TRUE | 0
3 | 1 | rule1 | sadfa | rtyRule1 | FALSE | 0
2 | 1 | Test rul 5 | SELECT ProfileTable.ProfileID, FLOOR(ProfileTable.Datefield) AS DayValue, @RuleSetNo,@RuleNo, AVG(Detail.StdevUnitsRead) AS DetailValue FROM ProfileTable INNER JOIN LinkTable ON ProfileTable.ProfileID = LinkTable.ProfileID INNER JOIN (SELECT DatePart(mm, DateField) AS Month, AVG(Unitsread) AS AvgUnitsRead, IsNull(STDEV(UnitsRead) ,0) AS StdevUnitsRead, ProfileTable.ProfileID FROM ProfileTable INNER JOIN linktable ON profiletable.profileid = linktable.profileId WHERE linktable.GroupID = @GroupID AND linktable.profileID <> 0 GROUP BY DatePart(mm, DateField), ProfileTable.ProfileID HAVING Count(UnitsRead)>1000 AND (Isnull(STDEV(Unitsread),0) < 0.5 * AVG(Unitsread) - 2.5 OR IsNull(STDEV(Unitsread),0) > 0.5 * AVG(Unitsread) + 5)) Detail ON ProfileTable.ProfileID = Detail.ProfileID AND DATEPART(mm, ProfileTable.Datefield) = Detail.Month WHERE (LinkTable.GroupID = @GroupID) AND (LinkTable.ProfileID <> 0) GROUP BY ProfileTable.ProfileID, FLOOR(ProfileTable.Datefield) | Test rule 5 | FALSE | 0
4 | 4 | The maximum value for the mean should be < 40 A | SELECT ProfileID, DATEADD(dd, DATEDIFF(dd, 0, DateField), 0) AS DayValue, @RuleSetNo,@RuleNo, Avg(Unitsread) as DetailValue FROM ProfileTable WHERE (ProfileID = @ProfileID) GROUP BY ProfileID, DATEADD(dd, DATEDIFF(dd, 0, DateField), 0) HAVING AVG(Unitsread)>40 | HighMean | TRUE | 0
4 | 7 | Identify areas without data | SELECT @ProfileId,datefield ,@RuleSetNo,@RuleNo,1 FROM DateTable WHERE (NOT (DateField IN (SELECT DISTINCT DATEADD(dd, DATEDIFF(dd, 0, DateField), 0) FROM ProfileTable WHERE ProfileId = @ProfileID))) AND (DateField > (SELECT MIN(Datefield) FROM ProfileTable WHERE ProfileId = @ProfileID)) AND (DateField < (SELECT MAX(Datefield) FROM ProfileTable WHERE ProfileId =@ProfileID)) | Absence | TRUE | 0
5 | 1 | Test absence of data in profile | SELECT @ProfileId,datefield ,@RuleSetNo,@RuleNo,1 FROM DateTable WHERE (NOT (DateField IN (SELECT DISTINCT DATEADD(dd, DATEDIFF(dd, 0, DateField), 0) FROM ProfileTable WHERE ProfileId = @ProfileID))) AND (DateField > (SELECT MIN(Datefield) FROM ProfileTable WHERE ProfileId = @ProfileID)) AND (DateField < (SELECT MAX(Datefield) FROM ProfileTable WHERE ProfileId =@ProfileID)) | Absence | TRUE | 0
6 | 1 | Identifies flat spots in channels (1 month where average is less than 0.02 A or max(units read)<0.15A ) | SELECT L.ProfileID, DateAdd(dd,DateDiff(dd,0,L.Datefield),0), @RuleSetNo, @RuleNo, Avg(R.AvgUnitsRead) FROM ProfileTable L INNER JOIN (SELECT ProfileTable.ProfileID, DateDiff(mm, 0,DateField) AS Month, AVG(UnitsRead) AS AvgUnitsRead, max(unitsread) as MaxUnitsRead FROM ProfileTable Where (ProfileTable.ProfileID = @ProfileID) and ProfileTable.ProfileId not in (Select ProfileId from Profiles where [Unit of measurement]=1) GROUP BY ProfileTable.ProfileId, DateDiff(mm, 0,DateField) HAVING AVG(UnitsRead) < 0.02 or Max(Unitsread)<0.150) R ON (DateDiff(mm, 0,DateField)= R.Month) where L.ProfileID=@ProfileID Group by L.ProfileID, DateAdd(dd,DateDiff(dd,0,L.Datefield),0) | Flatspot | TRUE | 0
6 | 3 | Identify spikes and floaters based on the following model: 4x+40>Max >4x-20 where x is consumption per day Or Max>90A | SELECT ProfileTable.ProfileID, DATEADD(dd, DATEDIFF(dd, 0, ProfileTable.DateField), 0) AS DayValue, @RuleSetNo,@RuleNo, Max(Unitsread) as DetailValue FROM ProfileTable WHERE (ProfileTable.ProfileID = @ProfileID) and ProfileTable.ProfileId not in (Select ProfileId from Profiles where [Unit of measurement]=1) GROUP BY ProfileID, DATEADD(dd, DATEDIFF(dd, 0, DateField), 0) HAVING ((select avg(unitsread) from profiletable where profileid=@ProfileId)*4 not between (Max(Unitsread)-40) and (Max(UnitsRead)+20)) or (Max(UnitsRead)>90) | Maximum | TRUE | 0
6 | 4 | The maximum value for the mean should be < 40 A | SELECT ProfileID, DATEADD(dd, DATEDIFF(dd, 0, DateField), 0) AS DayValue, @RuleSetNo,@RuleNo, Avg(Unitsread) as DetailValue FROM ProfileTable WHERE (ProfileID = @ProfileID) and ProfileTable.ProfileId not in (Select ProfileId from Profiles where [Unit of measurement]=1) GROUP BY ProfileID, DATEADD(dd, DATEDIFF(dd, 0, DateField), 0) HAVING AVG(Unitsread)>40 | HighMean | TRUE | 0
7 | 1 | Identifies flat spots in channels (1 month where average is less than 0.02 A or max(units read)<0.15A ) | SELECT L.ProfileID, DateAdd(dd,DateDiff(dd,0,L.Datefield),0), @RuleSetNo, @RuleNo, Avg(R.AvgUnitsRead) FROM ProfileTable L INNER JOIN (SELECT ProfileTable.ProfileID, DateDiff(mm, 0,DateField) AS Month, AVG(UnitsRead) AS AvgUnitsRead, max(unitsread) as MaxUnitsRead FROM ProfileTable Where (ProfileTable.ProfileID = @ProfileID) and ProfileTable.ProfileId in (Select ProfileId from Profiles where [Unit of measurement]=2) GROUP BY ProfileTable.ProfileId, DateDiff(mm, 0,DateField) HAVING AVG(UnitsRead) < 0.02 or Max(Unitsread)<0.150) R ON (DateDiff(mm, 0,DateField)= R.Month) where L.ProfileID=@ProfileID Group by L.ProfileID, DateAdd(dd,DateDiff(dd,0,L.Datefield),0) | I-Flatspot | TRUE | 0
6 | 7 | Identify areas without data | SELECT @ProfileId,datefield ,@RuleSetNo,@RuleNo,1 FROM DateTable WHERE (NOT (DateField IN (SELECT DISTINCT DATEADD(dd, DATEDIFF(dd, 0, DateField), 0) FROM ProfileTable WHERE ProfileId = @ProfileID))) AND (DateField > (SELECT MIN(Datefield) FROM ProfileTable WHERE ProfileId = @ProfileID)) AND (DateField < (SELECT MAX(Datefield) FROM ProfileTable WHERE ProfileId =@ProfileID)) | Absence | TRUE | 0
7 | 2 | Identify spikes and floaters based on the following model: 4x+40>Max >4x-20 where x is consumption per day Or Max>90A | SELECT ProfileTable.ProfileID, DATEADD(dd, DATEDIFF(dd, 0, ProfileTable.DateField), 0) AS DayValue, @RuleSetNo,@RuleNo, Max(Unitsread) as DetailValue FROM ProfileTable WHERE (ProfileTable.ProfileID = @ProfileID) and ProfileTable.ProfileId in (Select ProfileId from Profiles where [Unit of measurement]=2) GROUP BY ProfileID, DATEADD(dd, DATEDIFF(dd, 0, DateField), 0) HAVING ((select avg(unitsread) from profiletable where profileid=@ProfileId)*4 not between (Max(Unitsread)-40) and (Max(UnitsRead)+20)) or (Max(UnitsRead)>90) | I-Maximum | TRUE | 0
7 | 3 | The maximum value for the mean should be < 40 A | SELECT ProfileID, DATEADD(dd, DATEDIFF(dd, 0, DateField), 0) AS DayValue, @RuleSetNo,@RuleNo, Avg(Unitsread) as DetailValue FROM ProfileTable WHERE (ProfileID = @ProfileID) and ProfileTable.ProfileId in (Select ProfileId from Profiles where [Unit of measurement]=2) GROUP BY ProfileID, DATEADD(dd, DATEDIFF(dd, 0, DateField), 0) HAVING AVG(Unitsread)>40 | I-HighMean | TRUE | 0
7 | 4 | Identify areas without data | SELECT @ProfileId,datefield ,@RuleSetNo,@RuleNo,1 FROM DateTable WHERE (NOT (DateField IN (SELECT DISTINCT DATEADD(dd, DATEDIFF(dd, 0, DateField), 0) FROM ProfileTable WHERE ProfileId = @ProfileID))) AND (DateField > (SELECT MIN(Datefield) FROM ProfileTable WHERE ProfileId = @ProfileID)) AND (DateField < (SELECT MAX(Datefield) FROM ProfileTable WHERE ProfileId =@ProfileID)) | Absence | TRUE | 0
1 | 2 | Identifies flat spots in channels (1 month where average is less than 0.02 A or max(units read)<0.15A ) | SELECT L.ProfileID, DateAdd(dd,DateDiff(dd,0,L.Datefield),0), @RuleSetNo, @RuleNo, Avg(R.AvgUnitsRead) FROM ProfileTable L INNER JOIN (SELECT ProfileTable.ProfileID, DateDiff(mm, 0,DateField) AS Month, AVG(UnitsRead) AS AvgUnitsRead, max(unitsread) as MaxUnitsRead FROM ProfileTable Where (ProfileTable.ProfileID = @ProfileID) and ProfileTable.ProfileId in (Select ProfileId from Profiles where [Unit of measurement]=2) GROUP BY ProfileTable.ProfileId, DateDiff(mm, 0,DateField) HAVING AVG(UnitsRead) < 0.02 or Max(Unitsread)<0.150) R ON (DateDiff(mm, 0,DateField)= R.Month) where L.ProfileID=@ProfileID Group by L.ProfileID, DateAdd(dd,DateDiff(dd,0,L.Datefield),0) | I-Flatspot | TRUE | 0
8 | 2 | Identify spikes and floaters based on the following model: 4x+40>Max >4x-20 where x is consumption per month Or Max>90A | SELECT L.ProfileID, dayfield, @RuleSetNo, @RuleNo, R.mean FROM PQDayStats l INNER JOIN (SELECT DateDiff(mm, 0, DayField) AS Month, AVG(avgunits) mean, MAX(maxunits) maxi FROM PQDayStats p WHERE (ProfileID = @profileid) AND ProfileId IN (SELECT ProfileId FROM Profiles WHERE [Unit of measurement] = 2) GROUP BY profileid, DateDiff(mm, 0, DayField) HAVING sum(cntunits)> 0.7* 720 AND AVG(avgUnits) * 4 NOT BETWEEN MAX(MAXUnits) - 40 AND MAX(MAXUnits) + 20 AND MAX(maxunits) < 90) R ON DATEDIFF(mm, 0, l.Dayfield) = R.Month WHERE (l.ProfileID = @profileid) | I-Maximum | TRUE | 0
8 | 3 | The maximum value for the mean should be < 40 A | SELECT ProfileID, Dayfield, @RuleSetNo, @RuleNo, AvgUnits AS DetailValue FROM PQDayStats WHERE (ProfileID = @Profileid) AND (ProfileID IN (SELECT ProfileId FROM Profiles WHERE [Unit of measurement] = 2)) AND (AvgUnits > 40) and (cntunits > 0.7*288) | I-HighMean | TRUE | 0
8 | 4 | Identify areas without data | SELECT @ProfileId,datefield ,@RuleSetNo,@RuleNo,1 FROM DateTable WHERE (NOT (DateField IN (SELECT DISTINCT DATEADD(dd, DATEDIFF(dd, 0, DateField), 0) FROM ProfileTable WHERE ProfileId = @ProfileID))) AND (DateField > (SELECT MIN(Datefield) FROM ProfileTable WHERE ProfileId = @ProfileID)) AND (DateField < (SELECT MAX(Datefield) FROM ProfileTable WHERE ProfileId =@ProfileID)) | Absence | TRUE | 0
8 | 5 | Identify spikes and floaters based on the following model: 0.5x-2.5> Stdev >0.5x+5 where x is consumption per month | SELECT L.ProfileID, dayfield, @RuleSetNo, @RuleNo, R.mean FROM PQDayStats l INNER JOIN (SELECT DateDiff(mm, 0, DayField) AS Month, AVG(avgunits) mean, MAX(maxunits) maxi FROM PQDayStats p WHERE (ProfileID = @profileid) AND ProfileId IN (SELECT ProfileId FROM Profiles WHERE [Unit of measurement] = 2) AND cntunits = 288 GROUP BY profileid, DateDiff(mm, 0, DayField) HAVING sum(cntunits)> 0.7* 720 AND sqrt(1e-6 + avg(avgunits*avgunits + sdunits*sdunits) - avg(avgunits)*avg(avgunits)) NOT BETWEEN AVG(avgUnits) * 0.5 - 2.5 and AVG(avgUnits) * 0.5 + 5) R ON DATEDIFF(mm, 0, l.Dayfield) = R.Month WHERE (l.ProfileID = @profileid) | I-stdev |  | 0
8 | 6 | Voltage should always be between 47 and 276 | SELECT ProfileID, Dayfield, @RuleSetNo, @RuleNo, AvgUnits AS DetailValue FROM PQDayStats WHERE (ProfileID = @Profileid) AND (ProfileID IN (SELECT ProfileId FROM Profiles WHERE [Unit of measurement] = 1)) AND (MaxUnits > 276) AND (MinUnits < 47) | V-range |  | 0
4 | 1 | Identifies flat spots in channels (1 month where average is less than 0.02 A) | SELECT L.ProfileID, DateAdd(dd,DateDiff(dd,0,L.Datefield),0), @RuleSetNo, @RuleNo, Avg(R.AvgUnitsRead) FROM ProfileTable L INNER JOIN (SELECT ProfileTable.ProfileID, DateDiff(mm, 0,DateField) AS Month, AVG(UnitsRead) AS AvgUnitsRead, max(unitsread) as MaxUnitsRead FROM ProfileTable Where (ProfileTable.ProfileID = @ProfileID) GROUP BY ProfileTable.ProfileId, DateDiff(mm, 0,DateField) HAVING AVG(UnitsRead) < 0.02 or Max(Unitsread)<0.150) R ON (DateDiff(mm, 0,DateField)= R.Month) where L.ProfileID=@ProfileID Group by L.ProfileID, DateAdd(dd,DateDiff(dd,0,L.Datefield),0) | FlatSpot | TRUE | 0
4 | 3 | Identify spikes and floaters based on the following model: 4x+40>Max >4x-20 where x is consumption per day Or Max>90A | SELECT ProfileTable.ProfileID, DATEADD(dd, DATEDIFF(dd, 0, ProfileTable.DateField), 0) AS DayValue, @RuleSetNo,@RuleNo, Max(Unitsread) as DetailValue FROM ProfileTable WHERE (ProfileTable.ProfileID = @ProfileID) GROUP BY ProfileID, DATEADD(dd, DATEDIFF(dd, 0, DateField), 0) HAVING ((select avg(unitsread) from profiletable where profileid=@ProfileId)*4 not between (Max(Unitsread)-40) and (Max(UnitsRead)+20)) or (Max(UnitsRead)>90) | Maximum | TRUE | 0
4 | 5 | Identify floaters and spikes based on the folllowing model: 0.5*x+5>Stdev(per period) >0.5*x-2.5 | SELECT ProfileTable.ProfileID, DATEADD(dd, DATEDIFF(dd, 0, ProfileTable.DateField), 0) AS DayValue, @RuleSetNo,@RuleNo, Stdev(Unitsread) as DetailValue FROM ProfileTable WHERE (ProfileTable.ProfileID = @ProfileID) GROUP BY ProfileID, DATEADD(dd, DATEDIFF(dd, 0, DateField), 0) HAVING (select avg(unitsread) from profiletable where profileid=@ProfileId)*0.5 not between (Stdev(Unitsread)-5) and (Stdev(UnitsRead)+2.5) | StandardDeviation | TRUE | 0

## power-quality-rules-sets
RuleSetNo | Description | PrepareSQL | lock
1 | Tests |  | 0
2 | Dummy |  | 0
4 | Residential rules |  | 0
3 | rty |  | 0
5 | Absence only |  | 0
6 | Residential rules rev 20031103 |  | 0
7 | L&G Smallscale |  | 0
8 | L&G | exec PQmakedaystats @groupid=@groupid | 0